## 835-2020-80837808
Batch | EUDKVE-21058488 |  |  |  | Version: 112020
Sagsnavn | Gudbjerg Vandværk - Vandværket
Sagsnummer/lokalitetsnr
Udtagningsdato | 2021-06-02 10:15
Modtaget på laboratoriet | 2021-06-02 21:22
Rapport (seneste rapportrevision) | 11-06-2021/AR-21-CA-21058488-01
Prøvenummer | 835-2020-80837808
Prøve mærke | Afgang vandværk
DGUnr
Komponent | Resultat | Enhed | DL | Metode
Farvetal, Pt | 4.9 | mg Pt/l | 1 | DS/EN ISO 7887:2012, metode C
Turbiditet | 0.1 | FNU | 0.05 | DS/EN ISO 7027-1: 2016.
Coliforme bakterier 37°C | < 1 | MPN/100 ml | 1 | ISO 9308-2:2012
Escherichia coli | < 1 | MPN/100 ml | 1 | ISO 9308-2:2012
Kimtal ved 22°C | 4 | CFU/ml | 1 | ISO 6222:1999
Jern (Fe) | < 0.01 | mg/l | 0.01 | SM 3120 ICP-OES
2,4-dichlorphenol | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
2,6-dichlorphenol | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
2,6-DCPP (2-(2,6-dichlorphenoxy-propionsyre)) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
2,6-dichlorbenzosyre | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
4-CPP | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Alachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
AMPA (Aminomethylphosphorsyre) | < 0.01 | µg/l | 0.01 | M 8270 LC-MS/MS
Atrazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, 2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, deisopropyl-2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl-2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl-desisopropyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desisopropyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, didealkyl-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
BAM (2,6-dichlorbenzamid) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Bentazon | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chloridazon, desphenyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chloridazon, methyl-desphenyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chlorothalonil-amidsulfonsyre (CTA) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Desethyl-terbutylazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dichlobenil | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
Dichlorprop (2,4-DP) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dimethachlor ESA (CGA 354742) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dimethachlor OA (CGA 50266) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Diuron | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Ethylenthiourea (ETU) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Glyphosat | < 0.01 | µg/l | 0.01 | M 8270 LC-MS/MS
Hexazinon | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
MCPA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Mechlorprop (MCPP) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl CGA 108906 | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl CGA 62826 | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl-M | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metazachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metazachlor OA (479-4) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-desamino | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-desamino-diketo | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-diketo | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
N,N-dimethylsulfamid, DMS | 0.086 | µg/l | 0.01 | M 0336 LC-MS/MS
Propachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Simazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Simazin, 2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
4-nitrophenol | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
1,2,4-triazol | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Akkrediteret prøvetagning | Ja |  |  | DS ISO 5667-5,MST - Drikkevand. Manual for prøvetagning (v4, 201 N/A
pH | 7.4 | pH |  | DS/EN ISO 10523:2012
Prøvetagning efter flush | Udført |  |  | DS ISO 19458,DS ISO 5667-5,MST - Drikkevand. Manual for prøvetagning (v4, 201 N/A
Vandtemperatur | 10.1 | °C |  | DS/EN ISO 19458:2006
Ledningsevne ved 20°C | 540 | µS/cm | 15 | DS/EN 27888:2003 (ved 20°C)
Prøvens lugt | Ingen
Prøvens smag | Normal